## Sheet1
| BESS SIZING CALCULATIONS | [22 empty] | Inverters
| Turbina | Avg daily |  | 30 mins | Avg | Curtailed | Charging | Charging | Daily | Target | Minimum | Adjusted | Planned | Minimum | Minimum | Adjusted | Available | Daily | Daily | Annual | Internal | Amount | Capacity |  |  |  | Available | Available | Available
| 100% | Excess | Internal | turbine | Wind | Wind 10% | Demand | Demand | Charge | Capacity | Capacity | Target | Capacity | Charge | Charge | Min Charge | Capacity | Charge | Discharge | Discharge | Use | Sold | Utilization | # | cada | total | Capacity | Capacity | Capacity
| MW | MWh | Mwh | MWh | MWh /day | MWh/day | GWh /year | MWh/day | MWh | MWh | MW | MWh | MWh | MWh | % | MWh | MWh | MWh | MWh | GWh | GWh | GWh | % |  | MW | MW | MW | Minutes-Y1 | Minutes -Y25
São Miguel | 7.7 | 4.2688 | 1.9808 | 3.85 | 80.5479 | 8.0548 | 3.2313 | 8.8529 | 8.8529 | 14.9446 | 10 | 24 | 24.438 | 6.2938 | 30% | 7.3314 | 15.8847 | 8.8529 | 7.5781 | 2.766 | -0.723 | 2.043 | 55.73% | 4 | 3.06 | 12.24 | 7.9424 | 19.8559 | 14.8919
Terceira | 6.1 | 8.7232 | 0.95068 | 3.05 | 120.5479 | 12.0548 | 2.632 | 7.211 | 7.211 | 12.0717 | 5 | 15 | 15.045 | 4.5545 | 30% | 4.5135 | 9.7792 | 7.211 | 6.1726 | 2.253 | -0.347 | 1.906 | 73.74% | 3 | 2.66 | 7.98 | 4.8896 | 24.4481 | 18.3361
Pico | 3.376 | 8.9218 | 0.95068 | 1.688 | 32.3288 | 3.2329 | 4.7835 | 13.1054 | 13.1054 | 17.4039 | 3.3333 | 17.4039 | 15.045 | 3.1925 | 21.2% | 3.1895 | 11.1032 | 11.1032 | 9.5043 | 3.4691 | -0.347 | 3.1221 | 100% | 3 | 2.66 | 5.33 | 5.33 | 39.975 | 29.9813
Faial | 3.697 | 8.5998 | 0.87397 | 1.8485 | 28.4932 | 2.8493 | 4.4979 | 12.3231 | 12.3231 | 16.6724 | 3.3333 | 16.6724 | 15.045 | 3.353 | 22.25% | 3.3475 | 10.9452 | 10.9452 | 9.3691 | 3.4197 | -0.319 | 3.1007 | 100% | 3 | 2.66 | 5.33 | 5.33 | 39.975 | 29.9813
São Jorge | 1.54 | 3.2545 | 0.46301 | 0.77 | 30.137 | 3.0137 | 2.4569 | 6.7312 | 6.7312 | 8.825 | 1.6667 | 8.825 | 8.146 | 1.5846 | 20% | 1.6292 | 6.1095 | 6.1095 | 5.2297 | 1.9089 | -0.169 | 1.7399 | 100% | 2 | 2.66 | 2.66 | 2.66 | 39.9 | 29.925
Santa Maria | 1.811 | 1.4996 | 0.29041 | 0.9055 | 18.0822 | 1.8082 | 1.3134 | 3.5983 | 3.5983 | 5.2986 | 0.83333 | 5.2986 | 5.015 | 1.407 | 30% | 1.5045 | 3.2597 | 3.2597 | 2.7903 | 1.0185 | -0.106 | 0.91248 | 100% | 1 | 2.66 | 2.66 | 1.6299 | 48.8963 | 36.6722
Todas as Ilhas | 24.224 | 35.2677 | 5.5096 | 12.112 | 310.137 | 31.0137 | 18.915 | 51.8218 | 51.8218 | 75.2162 | 24.1667 | 87.1999 | 82.734 | 20.3854 | 26.01% | 21.5157 | 57.0816 | 47.4816 | 40.6442 | 14.8351 | -2.011 | 12.8241 | 90.79% | 16 |  | 36.2 | 27.7818
PARAMETERS FOR STUDIES
| Demand | Micro (autoconsumo) |  | PV - Others | PV - FA | Wind | Geothermal | Hydro | Waste | Biogas | BESS MWh | BESS MW
Sao Miguel | 551.7 | 16.8 |  | 16 | 36.01 | 35.54 | 271.56 | 24.33 | 33.93 | 0.6 | 24.438 | 7.9424
Terceira | 212.9 | 6.7 |  | 6.2 | 19.3 | 50.06 | 15 | 2.19 | 12.52 |  | 15.045 | 4.8896
Pico | 68.4 | 2.61 |  | 1.5 | 14.76 | 10.96 |  |  |  |  | 15.045 | 5.33
Faial | 63.3 | 2.42 |  | 1.64 | 13.85 | 8.44 |  |  |  |  | 15.045 | 5.33
Sao Jorge | 37.7 | 1.452 |  | 1.1 | 6.19 | 9.24 |  |  |  |  | 8.146 | 2.66
Santa Maria | 25.3 | 0.8712 |  | 1.22 | 3.26 | 6.81 |  |  |  |  | 5.015 | 1.6299
27.7818